## Sheet1
ELECTRICAL & ALLIED WORKS for AT 1st floor Ewart House,Fort Mumbai
BOQ
No. | Description | QTY | UNIT | RATE | AMOUNT
A | MAIN PANEL / MCCB DB'S
1 | ( MAIN ELECTRICAL LT PANEL )
INCOMER
Supply and installation / Testing / Commissioning of main LT Panel, wall/floor mounted/operated, totally enclosed vermin proof, indoor non draw out - cubicle type power panel fabricated out of 2 mm thick CRCA sheet having gasketed hinged cover on each cubicle fully powder coated / enamel painted after seven tank treatment incorporating horizontal and vertical sleeved copper bus bars complete with all internal wiring danger board, two earthing lugs, cable chamber etc. as required housing below mentioned switchgears / meters. (GA drawing of the panel to be got approved from the consultant)
a | INCOMER / OUTGOING
a) 1 Nos. 315A, TPN, MCCB, 36 ka Incomer
b) 3Nos. 100 AMPS 25 Ka TPN MCCB
c) 4 Nos. 63Amps TPN MCB
d) 2 Nos. 63Amps DP MCB,
e) 1 set TPN copper bus bar of 400A capacity.
f) (4 pole) g) 1 set, RYB indicating lamp with register and fuses.) A meter with selector switch, 3nos. of class 1.5, 200/5A, 10.0VA CTS
g) Volt Meter with selector switch Class.
| Full Set as above | 1 | Nos.
2 | Supply and installation / Testing / Commissioning of 70 KVAR APFC Panel, wall/floor mounted/operated, totally enclosed vermin proof, indoor non draw out - cubicle type power panel fabricated out of 2 mm thick CRCA sheet having gasketed hinged cover on each cubicle fully powder coated / enamel painted after seven tank treatment incorporating horizontal and vertical sleeved copper bus bars complete with all internal wiring danger board, two earthing lugs, cable chamber etc. as required housing below mentioned switchgears / meters. (GA drawing of the panel to be got approved from the consultant)
| Full Set as above | 1 | Nos. |  | 0
3 | Supply, Installation, Testing & Commissioning (SITC) of
| 400 Amps TPN MCCB with enclosure in meter room. | 1 | Nos.
4 | Suply and installation of 6- way, TPN Metal type, with plain / Transperant Door ( As approved by client / consulunt / architect ), UPS Power Distribution Board (UPDB ), surface / flush mounted on wall, interconnected wiring complete with earthing lugs including DB wiring dressing with ferruling, termination of circuits with ping type luggs, etc. housing following switchgears. ( Schneider/Hager/Legrand/ Simens / L&T make )
(Note :- DB size & type selection shall be done with referance to the total number of modul / poles avaible in the DB which shall be sutable for housing of below mentioned switchgears & components forming a complete set.)
a | 1 no. 63A, DP MCB "C" curve type as incomer
b | 18 nos. 16/25/32A, SP MCB "C" curve type as outgoings
| Full Set as above | 2 | Nos. |  | 0
5 | Suply and installation of 6- way, TPN Metal type, with plain / Transperant Door ( As approved by client / consulunt / architect ), Lighting/RAW Power Distribution Board ( L/RPDB-outgoing), (fo desks),surface / flush mounted on wall, interconnected wiring complete with earthing lugs including DB wiring dressing with ferruling, termination of circuits with ping type luggs, etc. housing following switchgears. ( Schneider/Hager/Legrand/ Simens / L&T make )
a | 1 no. 63A, TPN MCB "C" curve type as incomer
b | 18 nos. 16/20A, SP MCB "C/D" curve type as outgoings
| Full Set as above | 2 | Nos. |  | 0
6 | Suply and installation of 20/32A, DP, MC, box with 20A, metalclad / modular plug-socket for Split/Cassette A/Cs to be fixed on ceiling with support of M.S.angle/wooden bracket inclucing all necessary hardware & accessories, etc. ( Schneider/Hager/Legrand/ Simens / L&T make ) | 6 | Nos.
7 | Suply and installation of 63A, TPN MCB with Enclosure box for terminating supply to UPS i/p - o/p alongwith all necessary hardware & accessories, etc. complete as required.( Schneider/Hager/Legrand/ Simens / L&T make ) | 1 | Nos. |  | 0
8 | Supply and Installation of 6 way VTPN with 4 nos of 63Amp TP MCB for AC outgoing as below: | 1 | Nos |  | 0
Suply and installation of 63A, DP MCB with Enclosure box for terminating supply to UPS o/p alongwith all necessary hardware & accessories, etc. complete as required.( Schneider/Hager/Legrand/ Simens / L&T make )
9 | Supply & Installation of 63Amp TPN MCB in weather proof box for outdoor supply to AC | 4 | Nos
TOTAL OF SECTION (A)
B | CABLES / MAINS
1 | Suply and installation of 1100V grade armoured cable having sector / circular shaped aluminium / copper conductor PVC insulated cores, laid up, PVC tape wrapped inner sheathed, GI strip / wire armoured and ovrall extruded PVC sheathed confirming to IS: 1554, laid on wall / ceiling using GI clamps & spacers as per route shown at site and further as directed by consultant at site in the following sizes :- (Make - polycab/Finolex/CCI/RR/Havells.)
NOTE :- All Armoured cables shall be provided with labelling at every 5mtrs & then finaly with metal indentification tags showing the size & the location from/to the respective Panel / DB, at both the ends.
1.1 | 3 1/2 C x 95 Sq.mm Aluminium Armoured cable with 2 runs of 8 SWG GI bare wire ( main Incomer ) | 50 | Mtrs. |  | 0
1.2 | 4 C x 25 Sq.mm Aluminium Armoured cable with 2 runs of 12 SWG GI bare wire for AC | 150 | Mtrs. |  | 0
1.3 | 4 C x 16 Sq.mm Aluminium Armoured cable with 2 runs of 12 SWG GI bare wire | 0 | Mtrs.
1.4 | 4 C x 16 Sq.mm Copper Armoured cable with 2 runs of 12 SWG GI bare wire | 50 | Mtrs. |  | 0
1.5 | 4 C x 10 Sq.mm Copper Armoured cable with 2 runs of 12 SWG GI bare wire | 70 | Mtrs. |  | 0
1.6 | 1 C x 10 Sq.mm Copper Flexible cable for UPS In and output supply | 45 | Mtrs. |  | 0
1.7 | 4 C x 6 Sq.mm Copper Armoured cable for | 200 | Mtrs.
1.8 | 3 C x 4 Sq.mm Copper Armoured cable for | 100 | Mtrs.
1.9 | 3 C x 2.5 Sq.mm Copper Armoured cable for | 20 | Mtrs. |  | 0
2 | CABLE END TERMINATION
2.1 | 3 1/2 C x 120 Sq.mm Alu. amoured cable Gland Lug termination | 2 | Nos |  | 0
2.2 | 4 C x 25 Sq.mm Aluminium Armoured cable Gland Lug termination | 6 | Nos
2.3 | 4 C x 16 Sq.mm Aluminium Armoured cable Gland Lug termination | 10 | Nos
2.4 | 4 C x 16 Sq.mm Copp. Armoured cable Gland Lug termination | 8 | Nos
2.5 | 4 C x 10 Sq.mm Copper Armoured cable Gland Lug termination | 4 | Nos
2.6 | 3Cx6Sqmm copper flexible cable | 10 | Nos
2.6 | 1 C x 10 Sq.mm Copper Flexible cable Gland Lug termination | 16 | Nos
2.7 | 4 C x 6 Sq.mm Copper Armoured cable Gland Lug termination | 8 | Nos
2.8 | 3 C x 4 Sq.mm Copper Armoured cable Gland Lug termination | 8 | Nos
2.9 | 3 C x 2.5 Sq.mm Copper Armoured cable Gland Lug termination | 16 | Nos
TOTAL OF SECTION (B)
C | INTERNAL LIGHTING & POWER WIRING
1 | Supply & Installation of concealed / ressessed / surface light point / fan point / call bell point wiring using 600v FRLS grade 3R (P+N+E) x 1.5 sqmm copper conductor PVC insulated wires (with proper R,Y,B color code ) pulled through haevy gauge PVC conduits laid concealed over false ceiling or in wall chases on the celing including including 3R (P+N+E) x 2.5 sqmm circuit wires from the relevant DB and also including 2.5 sqmm green color copper earth wire and approved make modular type switch plate, switches, MS. concealed back box, etc as required & as approved by the consultant .(Each circuit shall not feed t more than 8 points 800 watts as per following configuration (The items rate shall include Lighting / Raw / UPS Power Circuit wiring from relevent DB to the switch board with 3Rx2.5 Sq.mm FRLS wire & from switch board to next switch board OR to the first light point / primary point / full point)
2 | Suply and installation of point wiring for UPS or stabilized power plug points on workstations / table for compturs using 3C x 2.5 Sq.mm FRLS grade copper conductor PVC sheathed white color flexible cable pulled throughh already laid floor raceways and taken up to table top using PVC rigid or flexible conduits run within wooden/metal partition. Each point consisting of 3 nos of 5A, 2/3 pin sockets above table top & 1 no. 15A switch above table top, wired together forming one point. The earth wire of 3 core flexible cable to be of yellow-green color only ( maximum 5 nos. desks served by one circuit from DB ) | 110 | Nos
TOTAL OF SECTION (C)
D | TRENCHING / FLOOR - RACEWAYS
1 | Supply & laying Raceway / Conduits (for under floor trenches/on trays) on existing flooring. Raceways / conduits shall be fixed to the flooring with GI clamps for finished levels as per the site conditions or through partitions with all accessories. The rate shall include preparation of treanches of required sizes by carefully removing the malva on exsiting floor for laying Rceways/conduits for power , data, telephone cables etc. The depth of the trenches shall be at least 2 inches from the finished floor level or up to RCC of the slab The rate shall include the cost of the Raceways/Conduit. The rate shall also include the activity of clearing the debris generated from the preparation of trenches & filling the same with PCC. (FOR THE PORTION WITHOUT FALSE FLOORING)
1.1 | 100 x 40 x 1.6mm thick Aluminium Raceways | 125 | Mtrs.
1.2 | 80 x 40 x 1.6mm thick Aluminium Raceways | 75 | Mtrs.
1.3 | 60 x 40 x 1.6mm thick Aluminium Raceways | 30 | Mtrs.
1.4 | 25 mm heavy guage PVC conduit to be laid concelled / surface in / on wall / floor as required as per the above mentional specifications | 150 | Mtrs.
NOTE :- 1. Only FRLS grade conductor wire shall be used; 2. Conduit carrying circuit wiring should not carry point wiring and Conduit carrying point wiring should not carry submain/circuit wiring; 3. Flexible conduits & Elbows are not allaowed; 4. The wire from ceiling junction to light point / light fixture shall be drawn in flexible PVC conduit with adaptor & cover for junction box & crimp type lugs at both the ends aloungwith necessary hardware & acccessories, etc. as required; 5. Proper ferrules, lugs, must be used in all cabling and wiring on both load / source ened; 6. Each switch board must be provided with respective ferrules representing the respective DB, phase & Circuit numbers; 7 Looping of Neutral / Earth wire between two seperate circuit on similar or other phase is strictly not allowed; 9. Ferulling / numbering / taggning to wires with circuit number & db name for all lighting & raw / ups power shall be strictly followed at both DB & switch board / switch socket boards ends.
1.1 | Primary light points including the cost of 5 A switch | 40 | Nos.
1.2 | Secondary light points looped from the above point | 80 | Nos.
1.3 | Bell point comprising of wiring as above including G-Magic wireless Door Bell 4061 with Remote, 32-Melodies & flashing Light. | 4 | Nos.
1.4 | 5 A plug point as primary point independent mounted on wall / partition / on work station etc. (RAW Power) | 20 | Nos.
1.5 | Secondary 5 A plug point on switch board or or looped from above 5 A primary point ( RAW Power ) ( Only five workstation / independent mounted raw power point shall be looped in one raw power circuit. Wheareas, four nos. of 5A s/s raw points will be considerd as secondary points & 1 no. of 5A s/s raw point will be considered as primary point.) | 46 | Nos.
1.6 | 5/15 A plug point as primary point independent mounted on wall / partition / on work station etc. (RAW Power) | 10 | Nos.
2 | Supply & Installation of floor Junction boxes without top cover for above raceways, of following sizes, fabricated out of M.S. sheet, fully powder coated with provision for removable M.S. / S.S. screwed cover p[lates on all four sides for blocking the entry into the junction box. All the junction boxes to be (with stud) properly earth - bounded with the raceway pipe using 12 SWG copper bare wire as directed at site.
2.1 | Junction Box of size (250mm x 250mm x 50mm x 2.5mm thick) | 10 | Nos.
2.2 | Junction Box of size (300mm x 300mm x 50mm x 2.5mm thick) | 8 | Nos.
2.3 | Junction Box of size (350mm x 350mm x 50mm x 2.5mm thick) | 12 | Nos.
3 | Supply & Installation of sutable sizes 2mm thick removable cover plate screwed on all four sides of M.S. sheet, fully powder coated for blocking the entry into the the junction box. for following sizes of junction boxes with rounded corners as per the instruction given & sample approved by the client / architect / consultant at site. Cover plate shall have required nos. of 1 dia knockouts for flexible conduit outlets as per the requirement.
3.1 | for Junction Box of size (250mm x 250mm x 50mm x 2.5mm thick) | 10 | Nos.
3.2 | for Junction Box of size (300mm x 300mm x 50mm x 2.5mm thick) | 8 | Nos.
3.3 | for Junction Box of size (350mm x 350mm x 50mm x 2.5mm thick) | 12 | Nos.
4 | Supplying & fixing of 2mm thick G.I. Perforated type cable Trays of Asian / Profab Engineers approved make. The Cable tray shall be fixed to the ceiling / wall with MS angle support with 35mmx2mm thick GI slotted 'C' channel patti at an interval of 1 meter or the MS angle iron fabricated support depending upon the location The rate include the cost of Supports, hardware & accessories, etc. complete as required.
TOTAL OF SECTION (D)
E | LIGHTING FIXTURES
Supply & Installation of lighting fixtures with lamps as per the details below including necessary harware such as clamps, nuts, bolts, nails, screws and sunpension rods as required for fixing the fixtures in positions as directed by architect / consulant / client.
| Note :- All Light Fixtures, Fans, Exhaust Fans & other fittings samples shall be approved by the Client / Architect / Consultant before placing order to the light fixture Vendor / Supplier. All Light Fixtures shall be of Phillips / Wipro / GE make only unless & oterwise other makes are specified. Client / Architect / consulant reserves right to approve / select final Light Fixtures from any make as required. | 40
1 | LED Type Light Fixture suitable for Modular Ceiling
| Supply & Installation of (30-40W) ( 2' X 2' ) full lit panel type LED Mirror optic Light Fixture or design to suit interiors as approved by bank The Fitting shall be sutaible for grid / plain ceiling type & surface mounted / to be hanged from the ceiling type at the height approved by architect. ( CGL Cat No. :- LCTLR-36-FO-CDL, PHILIPS Cat No. :- RC 380B LED 30-4000 PSE OD WH, WIPRO Cat No. :-CRCO10R038HP57, GE Cat No. :- Maple GCR030.56 or equivalent category & model in Bajaj make as approved by Client / Architect / Consulant. ) |  | Nos.
2 | LED Type Light Fixture suitable for Modular/Plain Ceiling
| Supply & Installation of (15-18W) LED Spotlight flush mounted Light Fixture ( CGL / PHILIPS / GE ) as approved by Client / Architect / Consulant. ) | 55 | Nos.
3 | Supply & Installation of 20 W 4 fit LED Light Fixture ( CGL / PHILIPS / GE ) as approved by Client / Architect / Consulant. ) | 15 | Nos.
4 | Cove /special lights | 40 | nos
(Base Rate upto Rs3000/)
TOTAL OF SECTION (E)
F | DATA NETWORKING
1 | Supply & Installation of Data point including approved make Cat-6 UTP cable through aready laid trenches / conduits, RJ-45 information outlet, single / duil / quad type face plate, PVC back box etc. (with 25 years certification Termination, Testing and Documentation of UTP Points complete as required. CABLE d LINK CAT 6 | 2500 | MTR
| SITC of D link make cat 6 IO | 100 | Nos.
2 | Supply & Installation of 24 Port 10/100 Mbps manageable D'link switch. | 5 | Nos.
3 | Supply & Installation of 24 Port jack panel. | 5 | Nos.
4 | Supply of mounting cord (7 feet) | 110 | Nos.
5 | Supply of mounting cord (3 feet) | 110 | Nos.
6 | Supply & Installation of 42U Network server Rack including all necessary hardware, accessories, etc. | 1 | No.
7 | False flooring 600mm X600 mm unitile/equivalent for network cabling | 300 | Sq. ft
TOTAL OF SECTION (F)
G | VOICE NETWORKING
1 | Supply & Installation of Voice point including approved make Cat-6 UTP cable through aready laid trenches / conduits, RJ-45 information outlet, single / duil / quad type face plate, PVC back box etc. with Termination, Testing and Documentation of UTP Points complete as required. | 50 | Nos.
2 | Supply, Installation,testing and commissioning of indoor type telephone Main Distribution Frame (MDF) / Box with sutable S.S. frame for mounting tag module, cable, wires and incorporated in 16 SWG MS box with proper lockable cover. The box should be fixed on wall with sutable fastners including painting & earthing. This also includes fixing the cable, distribution chart suffcient space for the cables, wires etc. to be provided ine the box :-
2.1 | Supply & Installation of 100 pair MDF with Krone module including all hardware & accessoried , etc. complete as required. | 1 | Nos. |  | 0
2.2 | Supply & Installation of 50 pair MDF with Krone module including all hardware & accessoried , etc. complete as required. | 1 | Nos.
2.3 | Supply & Laying of 100 pair telephone cable through heavy gauge pvc conduit including all necessary hardware & accessories , etc. | 105 | mtrs
2.4 | Supply & Laying of 50 pair telephone cable through heavy gauge pvc conduit including all necessary hardware & accessories , etc. | 90 | Rmt
TOTAL OF SECTION (G)
H | PUBLIC ADDRESS SYSTEM
1 | Supply, Installation, Testing, Commisioning of point wiring for music - cum PA system comprising of 2x 1.5 sq.mm strandes , copper conductor , flexible PVC insulated and PVC Sheathed wire pulled through 20 mm dia. PVC heavy gauge conduits and looped from one speaker to other and to the volume control switch wherver applicable and finally terminated and tagblock. | 16 | nos.
2 | Supply, Installation, Testing, Commisioning of 6" dia music speakers to be flushed mounted on false ceiling similar to BOSCH / approved equivalent make. All speakers to be equipped with matching transformer for direct connection to 100v output line. | 10 | Nos.
3 | Supply & Installation of Amplifier for PA system(65watt) | 1 | No
TOTAL OF SECTION (H)
I | Earthing
1 | Supply & Installation of chemical earthing for UPS | 2 | nos
2 | Supply and installation 25x3 mm copper earthe patty | 25 | mtr
3 | SWG 12 copper for earthing | 50 | mtr
TOTAL OF SECTION (I)
FINAL TOTAL AMOUNT (Rs.)=A+B+C+D+E+F+G+H+I
NOTE -1. L1 will be decided on the basis of Final Total Amount
2. GST will be paid as actual.
Makes :
Switchgear -legrand ,siemens ,L&T
Cables/wires : Polycab/RR/Finolex
Light Fixtures :Phillips
Data/Voice: D-link.
Switch/socket/:Anchor ROMA/MK
FAN :Crompton.